HIGH-SPEED ROLL-UP DOOR, type „EFA-SRT® CR Efficient“

Manufacture, delivery and installation of

Roll-up door with flexible curtain with low air loss for permanent industrial application in hygienic and clean rooms for application with limited installation spaces and low to medium GMP requirements.

The door system „EFA-SRT® CR Efficient“ is approved for usage in classified rooms up to ISO class 6 (DIN ISO 14644) acc. to TÜV SÜD for particle sizes >= 0.1 µm. With an air pressure difference of up to 30 Pa there is only an air loss of up to 40m³/h (depending on the size and installation side).

All visible steel parts of the self-supporting construction are powder coated according to RAL. Especially slim columns (75x100 mm) and the small head box (min. 380 mm) enable a very space-saving installation.

The drive (electric motor with integrated gear, brake and absolute encoder IP55) is connected in an axial way to the winding shaft; the control is a microprocessor-controlled control with frequency converter. All controller components incl. membrane keypad (Open-Stop-Close) and info display are integrated in the polycarbonate box with sizes 220 x 565 x 200 mm and protection type IP 65 next to the door.

By means of the absolute encoder a manual respectively automated synchronisation after first switch- on the door or after power failure is not required any more.

The curtain is made of 2 mm thick PVC coated, flexible polyester fabric (FDA approved, antistatic, silicon-free) which is rolled up onto a horizontally running, galvanised shaft.

Colours: papyrus-white similar to RAL 9018, light-grey similar to RAL 7035, signal-grey similar to RAL 7004.

The door curtain is held within the guidance (columns) by means of laterally fixed wind buttons onto the left and the right hand side of the door curtain.

Accident protection:

The scope of supply includes a photo cell fitted into the door frame as well as a self-monitoring safety contact bar according to DIN EN12453. Signal of the contact bar is sent by wireless radio transmission; an EMERGENCY STOP shock switch is attached to the frame as standard.

Emergency opening of the door e.g. in the case of power failure is possible on installation side of the opening via manual hand crank.

All regulations pursuant to DIN EN 13241-1 are complied with.

OPENING SPEED:	approx. 0.8 m/s

Max. DOOR LEAF SPEED	up to 1.0m/s

(Depending on door size)

CLOSING SPEED:	approx. 0.5 m/s

On-site connection to 230 V / 50-60 Hz. Fuse 16 A

With function test and commissioning for clear opening (max. W x H = 3,000 x 3,500 mm)

Width = ............... mm  x  Height = ............... mm

Manufacturer:

EFAFLEX Tor- und Sicherheitssysteme GmbH & Co. KG

www.efaflex.com