HIGH-SPEED TURBO DOOR, type “EFA-STT®”

Manufacture, delivery and installation of

High-speed turbo door, type „EFA-STT®“, with electro-mechanical high-performance door drive for permanent industrial application.

The door system mainly consists of:

Self-supporting lateral steel frames; steel parts generally galvanized, spiral-shaped door guidance

The load is transmitted on both sides: For achieving this, a synchronised shaft will be installed. For the exact, smooth and low-noise guidance of the hinge straps, ball-bearing precision rolling units have to be used. A sufficiently dimensioned tension spring mechanism, ensuring the weight balancing of the door leaf according to the standard DIN EN 12604 and a manual opening of the door (e.g. in the case of a power failure) is installed in the door frames.

The door leaf consists of a frame made of anodised aluminium as well as of a middle area which is made of transparent, single-walled acrylic glass. The visible surface of the door leaf must be at least 70%, and optical clarity must be ensured permanently.

This SPIRAL BODY is designed to guide the laths of the door leaf completely without contact and thus without wear and with best possible noise reduction.

The DOOR is driven by a geared motor which has to be developed as high-frequency motor. The positions of the door are permanently detected by means of non-wearing, inductive proximity switches, with the limits being determined electronically. Electro-mechanical limit switches are not permissible here.

OPENING SPEED:				up to approx. 2.5 m/s

Max. DOOR LEAF SPEED		up to approx. 3.0 m/s

(depending on door size)

CLOSING SPEED:				up to approx. 1.0 m/s

The MICROPROCESSOR CONTROL is installed together with the integrated frequency converter in a separate plastic switch cabinet, protection type IP 65. Connection to 230V and/or 400 V / 50 Hz power supply on-site.

The scope of delivery includes an electric Safety contact edge, self-monitoring according to DIN EN 12453: Its connection cable must be guided in a protective energy chain within the door frame.

Regulations pursuant to DIN EN 13241-1 are complied with;

Resistance to wind load pursuant to DIN EN 12424 up to class 4

(values depend on the door size and the equipment)

for clear opening dimensions

Width = ............... mm  x  Height = ............... mm

Manufacturer:

EFAFLEX Tor- und Sicherheitssysteme GmbH & Co. KG

www.efaflex.com